## WODetails
WO No | Task Name | Labour Name | Specifications | Qty | Unit Name | Conversion Factor | Rate | Tax Scheme Name | Retention % | Payment Schedule | Start Date | Completion Date | Credit Days | Rate Remark | Rate List Name
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6431_Providing and Laying Concealed Light Points Shall be carried-(No.) | Providing & Laying Concealed Light Points Shall be carried outwith 20 mm. PVC conduit Make -Precision ISI, with 1 sq.mm. FRLSH Single PVC Copper wire make- RR KABEL, with Modular Type 5- Amp Switch, Socket, Plate, & PVC Box, Make- Anchor Roma ISI, if required, Plug Shall be earthed with 1 sq.mm. copper wire, with necessary Holder, Ceiling rose, step connector, mounted on a round plate. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ | 3_C + S GST 0% URD | 2_Consultancy | 1_AGAINST RA BILL 100% | 10_Bag
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6432_Providing and Laying concealed Exhaust Fan Points, same as p-(No.) | Providing & Laying concealed Exhaust Fan Points, same as per Item no. 1 | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ | 5_C + S GST 12% IP | 1_Earth Work | 11_50%+50% | 13_Box
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6433_Do–do as above as per item No.1 but with 5- Amp 5 Pin plug-(No.) | Do – do as above as per item No.1 but with 5- Amp 5 Pin plug point on the Switch Board (Half Plug point) | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ | 1_C + S GST 18% IP |  | 12_50%+40%+5%+5% | 14_Brass
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6434_Providing and Laying concealed Fan Points with 2 Module-(No.) | Providing & Laying concealed Fan Points with 2 Module Step Regulator, (same as per Item No.1) | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ | 4_C + S GST 28% IP |  | 13_56%+44% | 128_Bundle
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6435_Providing and Laying concealed Bell point with 1 sq.mm.-(No.) | Providing & Laying concealed Bell point with 1 sq.mm. FRLSH single PVC copper wire, with 20 mm PVC conduit, with Modular Type Bell push, Plate, PVC Box, & Master Control Switch, (same Make – as per item No.1) | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ | 13_C + SGST 12% Input |  | 14_92.15%+7.85% (PERGOLA) | 1_Cft.
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6436_Providing and Laying concealed 5- Amp 5 Pin Plug Point-(No.) | Providing & Laying concealed 5- Amp 5 Pin Plug Point with 20 mm PVC conduit & 1 sq.mm X 2 Nos FRLSH single PVC copper wire, with 5- amp Switch, Socket, Plate, PVC box, including 1 sq.mm copper earthing wire Located at convenient Location (Same Make- as per item No. 1). Including circuit wiring | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ | 14_GST@12% |  | 15_20%+80% | 6_Cu. Mtrs
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6437_Providing and Laying concealed 15- Amp Domestic Plug Point-(No.) | Providing & Laying concealed 15- Amp Domestic Plug Point for uses Geyser, Fridge, Oven, Washing Machine, with 20 mm. PVC Conduit, with 2.5 sq.mm. X 2 Nos FRLSH single PVC Copper wire, with Modular Type 15- amp Switch, Socket, Plate, PVC Box, including 1.5 sq.mm. copper earthing wire (Same Make- as per No.1) | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ | 10_IGST 18% IP RD |  | 16_56.82%+43.18% (GATE) | 131_Cuft
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6438_Providing and Laying concealed A.C. Point with 4 sq.mm-(No.) | Providing & Laying concealed A.C. Point with 4 sq.mm X 2 Nos FRLSH single PVC copper wire, with 1.5 sq.mm copper earthing wire, with 20 mm PVC conduit, with Modular Type 20- Amp Switch, Socket, Plate, PVC Box, (Same Make- as per Item No.1) | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ | 6_IGST 28% IP RD |  | 17_90%+10% | 8_Cum
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6439_Supplying and Running Concealed Circuit, with 2.5 sq.mm-(Rft.) | Supplying & Running Concealed Circuit, with 2.5 sq.mm X 2 Nos FRLSH single PVC insulated 1100V grade copper conductor wires, make- RR KABEL ISI, Fun in 20 mm PVC conduit, make- Precision ISI, including 1.5 sq.mm green color PVC copper Earthing wire, From Main Distribution System to every switch board | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ | 11_Input I GST 12% |  | 18_100% ADVANCE | 3_Cum Sft.
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6440_Supplying and Running Concealed Circuit, with 4 sq.mm-(Rft.) | Supplying & Running Concealed Circuit, with 4 sq.mm X 2 Nos FRLSH single PVC insulated 1100V grade copper conductor wires, make- RR KABEL ISI, Fun in 20 mm PVC conduit, make- Precision ISI, including 1.5 sq.mm green color PVC copper Earthing wire, From Main Distribution System to every switch board | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ | 2_S+C GST 5%IP |  | 19_PLUMBING CONSULTANT (20%+30%+20%+20%+10% | 4_Day
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6441_Providing & laying concealed T.V. Cable Points with RG- 6-(No.) | Providing & laying concealed T.V. Cable Points with RG- 6, Co – Axial cables, make- RR KABEL ISI, Fun in 20 mm PVC conduit, make- Precision ISI, with modular Type TV. Socket, Plate, PVC box, make- Anchor Roma ISI | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 2_78% + 12% + 10% | 133_Ft.
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6442_Providing & Laying concealed Telephone Point with 0.5mm-(No.) | Providing & Laying concealed Telephone Point with 0.5mm 2-Pair Telephone wire make- RR-KABEL ISI, Fun in 20 mm PVC conduit, make- Precision ISI, with modular Type RJ-11 Telephone socket, Plate, PVC box, make- Anchor Roma ISI | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 20_LIFT (10%+60%+20%+10%) | 157_Hrs
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6443_Providing & Laying concealed Intercom Point with 0.5mm-(No.) | Providing & Laying concealed Intercom Point with 0.5mm 2-Pairs Intercom wire make- RR-KABEL ISI, Fun in 20 mm PVC conduit, make- Precision ISI, with modular Type RJ-11 Intercom socket Plate, PVC box, make- Anchor Roma ISI | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 21_DOWNTAKE PLUMBING 40%+60% | 143_inch
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6444_Providing & Laying concealed Internet Point with Cat - 6-(No.) | Providing & Laying concealed Internet Point with Cat - 6 wire, make- RR KABEL ISI, Fun in 20 mm PVC conduit, make- Precision ISI, with Modular Type- RJ-45 Internet Sockets, Plate, Box, make- Anchor Roma ISI | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 22_PLUMBING -10%+20%10%+10%+10%+10%+5%+10%+ | 5_Job
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6445_Video Door Phone Point concealed with 4+1 camera wire make--(No.) | Video Door Phone Point concealed with 4+1 camera wire make- RR KABEL ISI, Fun in 20 mm PVC conduit Make-Precision ISI | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 22_PLUMBING -13.34%+26.67%+13.33%+13.33%+13 | 11_Kg
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6446_Providing & Fixing Distribution Boards with 4 Ways TPN-(No.) | Providing & Fixing Distribution Boards with 4 Ways TPN Double Door 1 Nos box, and 40 Amp 4 Pole 30mA. 10kA. RCCB 1 Nos, with 16/20 Amp single Pole MCBs. 10kA. 9/12 Nos make- INDOASIAN ISI | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 23_AL WINDOW (10%+50%+35%+3%+2%) | 129_Lot
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6447_Providing & Fixing Distribution Boards with 12 Ways SPN-(No.) | Providing & Fixing Distribution Boards with 12 Ways SPN Double Door 1 Nos box, and 40 Amp 4 Pole 30mA. 10kA. RCCB 1 Nos, with 16/20 Amp single Pole MCBs. 10kA. 8/10 Nos make- INDOASIAN ISI | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 24_ERP 33.33%+66.66% | 139_Ltr
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6448_Providing & Fixing L.V. Distribution Board Double Door-(No.) | Providing & Fixing L.V. Distribution Board Double Door, with 4 Way Splitter and 10 Way Chrome Termination of T.V. cable & Telephone, Intercom Connections Provisions make- INDOASIAN ISI | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 25_Crystal Arch | 9_Ltr.
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6449_Supplying & Laying Concealed Three Phase Main Line-(Rft.) | Supplying & Laying Concealed Three Phase Main Line shall be carried out with 6 sq.mm X 4 Nos FRLSH single PVC insulated 1100V grade copper conductor wires, make- RR KABEL ISI, Fun in 25 mm. PVC conduit, make- Precision ISI, including 4sq.mm. green color PVC copper Earthing wire, From Meter Room to Flat inside Main Distribution board | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 26_ELECT. CONSULTANT (15%+20%+20%+20%+12.50 | 135_Lumsum
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6450_Supplying & Laying Concealed Single Phase Main Line-(Rft.) | Supplying & Laying Concealed Single Phase Main Line shall be carried out with 6 sq.mm X 2 Nos FRLSH single PVC insulated 1100V grade copper conductor wires, make- RR KABEL ISI, Fun in 25 mm PVC conduit make- Precision ISI, including 4 sq.mm green color PVC copper Earthing Wire from Meter Room to Flat Inside Main Distribution board | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 27_SIDDHIVINAYAK ELECTRICAL CONSULTANT | 130_Meter
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6451_Supplying & Laying Concealed T.V. Cable Main Line with RG- 6-(Rft.) | Supplying & Laying Concealed T.V. Cable Main Line with RG- 6 Co – Axial cables make- RR KABEL ISI, Fun in 25 mm PVC conduit, make- Precision ISI, From Electrical duct junction box to Flat Inside L.V. DB. Main Box | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 28_SIDDHIVINAYAK ELEC.CONSULTANT | 12_Metric Ton
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6452_Supplying & Laying Concealed Telephone Main Line-(Rft.) | Supplying & Laying Concealed Telephone Main Line with 0.5sq.mm 2 Pairs Telephone wire make- RR KABEL ISI, Fun in 25 mm PVC conduit make- Precision ISI, From ground Staircase/Meter room MTNL. Junction box to Flat inside Located at L.V. DB. Main Box | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 29_Scaffolding Fixing & Removing work | 147_ML
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6453_Supplying & Laying Concealed Intercom Main Line-(Rft.) | Supplying & Laying Concealed Intercom Main Line with 0.5sq.mm 2 Pairs Intercom wire make- RR KABEL ISI, Fun in 25 mm PVC conduit make- Precision ISI, from ground Staircase/Meter room Intercom Junction box to Flat inside Located at L.V. DB. Main Box | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 3_78% + 22% | 159_Month
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6454_Providing & Fixing 100 Pair krone Box from Staircase inside-(No.) | Providing & Fixing 100 Pair krone Box from Staircase inside/Meter room Fittings. (Only if required) | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 30_KEYSTONE | 142_MT
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6455_Supplying & Laying Concealed Internet Data Cable Main Line-(Rft.) | Supplying & Laying Concealed Internet Data Cable Main Line with Cat- 6 Internet Data cable wire, make- D - Link ISI, Fun in 25 mm PVC conduit, Make-Precision ISI, from Internet Junction box to Flat Inside Located at L.V. Box | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 31_BIG SLICE | 136_NA
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6456_Supplying & Laying Concealed CCTV Cable Wiring with CCTV-(Rft.) | Supplying & Laying Concealed CCTV Cable Wiring with CCTV CO-EX CABLE 4+1 pear Power supply cable make- RR KABEL ISI, Fun in 25 mm PVC conduit make- Precision ISI, from DVR to Camera of ground floor, Podium floor, & Passenger Lifts. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 32_FLOORING (95%+5%) | 158_NO
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6457_Supplying & Laying Concealed Intercom Main Line 0.5 sq.mm-(Rft.) | Supplying & Laying Concealed Intercom Main Line with 0.5 sq.mm 10 Pairs Intercom Armored cable make- RR KABEL ISI, Fun in Electric Chamber from Watchman Cabin to gr. Staircase inside Located at 100 pairs kroon Box | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 33_LIFT (10%+40%+40%+10%) | 7_No.
71 | 21519_SUPPLYING LAYING & FIXING CONCEALED WORK | 6458_Supplying and Laying Concealed Intercom Main Line-(Rft.) | Supplying & Laying Concealed Intercom Main Line with 0.5 sq.mm 100 Pairs Intercom Armored cable make- RR KABEL ISI, Fun in 4” PVC Pipe Electric Chamber from Intercom Junction box gr. Staircase inside Located at 100 pairs kroon Box | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 35_PS for Plumbing | 145_Pair
71 | 21520_COMMON AREA LOBBYS PODIUM GROUND | 6359_Providing & Laying Concealed Light Points for Staircase, Li-(No.) | Providing & Laying Concealed Light Points for Staircase, Lift Lobby, Stilt Parking, & Wall Compound and Entrance lobby, Servant Toilet, Podium, Security room etc. (same as per Item no. 1). | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 36_Paymnet Schedule 3D View | 146_Pcs
71 | 21520_COMMON AREA LOBBYS PODIUM GROUND | 6360_Providing and Laying concealed Fan Points with 2 Module Ste-(No.) | Providing & Laying concealed Fan Points with 2 Module Step Regulator, (same as per Item No. 5). | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 37_PS For Swimming Pool | 140_PKT
71 | 21520_COMMON AREA LOBBYS PODIUM GROUND | 6361_5- Amp Plug Point (same as per Item no.7)-(No.) | 5- Amp Plug Point (same as per Item no. 7) | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 38_Pilling Work | 134_Rft.
71 | 21520_COMMON AREA LOBBYS PODIUM GROUND | 6363_Fixing of Distribution Boards & Control switch-(No.) | Fixing of Distribution Boards & Control switch. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 39_40% & 60% | 161_Rig
71 | 21520_COMMON AREA LOBBYS PODIUM GROUND | 6364_A.C. Point Concealed with controlled by 20- Amp MCB switch-(No.) | A.C. Point Concealed with controlled by 20- Amp MCB switch. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 4_25% + 30% + 25% + 15% + 5% | 141_Ring
71 | 21520_COMMON AREA LOBBYS PODIUM GROUND | 6365_Providing & Fixing 2.5 sq.mm x 3 core Copper Armored cable-(Rft.) | Providing & Fixing 2.5 sq.mm x 3 core Copper Armored cable for Compound Lighting etc. Make- RR KABEL. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 40_Sumit One -PS | 127_RMT
71 | 21520_COMMON AREA LOBBYS PODIUM GROUND | 6366_Providing & Fixing 2.5 sq.mm x 4 core Copper Armored cable-(Rft.) | Providing & Fixing 2.5 sq.mm x 4 core Copper Armored cable for Meter Room to Watchman Cabin. Make- RR KABEL. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 41_Atulyam - PS | 2_Sft.
71 | 21520_COMMON AREA LOBBYS PODIUM GROUND | 6367_Main Line Staircase, Meter Room to Terrace 4 sq.mm x 4 Nos-(Rft.) | Main Line Staircase, Meter Room to Terrace 4 sq.mm x 4 Nos. | 12 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 42_RCC | 160_Shift
71 | 21520_COMMON AREA LOBBYS PODIUM GROUND | 6368_Main Line Staircase, Meter Room to Terrace 2.5 sq.mm X 3 No-(Rft.) | Main Line Staircase, Meter Room to Terrace 2.5 sq.mm X 3 Nos. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 43_PCE PS | 15_Slab
71 | 21520_COMMON AREA LOBBYS PODIUM GROUND | 6369_Intercom point, Lobby & Watchman cabin etc.-(No.) | Intercom point, Lobby & Watchman cabin etc. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 44_MEP KROMATICS | 144_Sq.ft
71 | 21520_COMMON AREA LOBBYS PODIUM GROUND | 6370_Main Line entrance lobby, Society office, 4 sq.mm X 3 Nos w-(Rft.) | Main Line entrance lobby, Society office, 4 sq.mm X 3 Nos wire with earth wire. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 45_Traffic Study | 132_SQMT
71 | 21521_FITTING & FIXTURE | 6371_Spot, Tube, & Panel Light Fixing.-(No.) | Spot, Tube, & Panel Light Fixing. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 46_STP PAYMENT SCHEDULE | 156_Trip
71 | 21521_FITTING & FIXTURE | 6372_Strip Light Fixing.-(Rft.) | Strip Light Fixing. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 47_MEP DESIGN CONSULTANT
71 | 21521_FITTING & FIXTURE | 6373_Exhaust Fan Fixing.-(No.) | Exhaust Fan Fixing. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 5_PLUMBING 10%+15%+10%+10%+15%+15%+10%+10%
71 | 21521_FITTING & FIXTURE | 6374_Fan Fixing.-(No.) | Fan Fixing. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 6_AGAINST RA BILL
71 | 21522_PASSENGERS LIFTS WORK | 6375_Providing & Laying 4 core 10 sq.mm Copper Armored Cable mak-(Rft.) | Providing & Laying 4 core 10 sq.mm Copper Armored Cable make- RR KABEL ISI with Saddle, Screw, & Rowel plug, from meter room to Lift Top Machine. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 7_Painting Work-30-30-40
71 | 21522_PASSENGERS LIFTS WORK | 6376_Providing & Laying 4 core 6 sq.mm Copper Armored Cable make-(Rft.) | Providing & Laying 4 core 6 sq.mm Copper Armored Cable make- RR KABEL ISI with Saddle, Screw, & Rowel plug, from meter room to Lift Top Machine. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 8_ELECT. 20%+25%+25%+25%+5%
71 | 21522_PASSENGERS LIFTS WORK | 6377_Providing & Laying 3 core 2.5 sq.mm copper Armored cable ma-(Rft.) | Providing & Laying 3 core 2.5 sq.mm copper Armored cable make- RR KABEL ISI with Saddle, Screw, & Rowel plug, from meter room to Lift Machine. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_ |  |  | 9_Granite Texture
71 | 21522_PASSENGERS LIFTS WORK | 6378_Providing & Laying 8 SWG X 2 NOS. Leads of Copper / GI. Ear-(Rft.) | Providing & Laying 8 SWG X 2 NOS. Leads of Copper / GI. Earth Conductor from Meter Room to Lift Machine Room. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21522_PASSENGERS LIFTS WORK | 6379_Providing & Fixing 63 Amp 4 Pole RCCB 300mA with 4-way DB b-(No.) | Providing & Fixing 63 Amp 4 Pole RCCB 300mA with 4-way DB box for Lift machine room Termination of 3 Phase cable Connection make- INDOASIAN. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21522_PASSENGERS LIFTS WORK | 6380_Providing & Fixing 63 Amp 4 Pole RCBO 300mA with 6-way DB b-(No.) | Providing & Fixing 63 Amp 4 Pole RCBO 300mA with 6-way DB box for Lift machine room Termination of 3 Phase cable Connection make- INDOASIAN. ( IF REQUIRED ) | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21522_PASSENGERS LIFTS WORK | 6381_Providing & Fixing 40/63 Amp 4 Pole RCB 10kA. with 4-way DB-(No.) | Providing & Fixing 40/63 Amp 4 Pole RCB 10kA. with 4-way DB box for Lift machine room Termination of 3 Phase Cable Connection make- INDOASIAN. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21522_PASSENGERS LIFTS WORK | 6382_Providing & Fixing 16/25 Amp 2 Pole RCBO 300mA with 4-way D-(No.) | Providing & Fixing 16/25 Amp 2 Pole RCBO 300mA with 4-way DB box for Lift machine room Termination of 1 Phase Cable Connection make- INDOASIAN ISI | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21522_PASSENGERS LIFTS WORK | 6383_Providing & Fixing 16/25 Amp 2 Pole MCB with 2-way DB box f-(No.) | Providing & Fixing 16/25 Amp 2 Pole MCB with 2-way DB box for Lift machine room Termination of 1 Phase Cable Connection make- INDOASIAN ISI | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21522_PASSENGERS LIFTS WORK | 6384_Providing & Fixing 25/40 Amp 4 Pole MCB with 4-way DB box f-(No.) | Providing & Fixing 25/40 Amp 4 Pole MCB with 4-way DB box for Lift machine room Termination of 1 Phase Cable Connection make- INDOASIAN ISI | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21522_PASSENGERS LIFTS WORK | 6385_Providing & Fixing Bulkhead Lamp fitting with 40 watts bulb-(No.) | Providing & Fixing Bulkhead Lamp fitting with 40 watts bulb in Lift shaft. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21522_PASSENGERS LIFTS WORK | 6386_Lights Point in lift shaft.-(No.) | Lights Point in lift shaft. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21522_PASSENGERS LIFTS WORK | 6387_Two Way Point in lift shaft.-(No.) | Two Way Point in lift shaft. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21522_PASSENGERS LIFTS WORK | 6388_5 Amp Plug Point in lift shaft.-(No.) | 5 Amp Plug Point in lift shaft. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21522_PASSENGERS LIFTS WORK | 6389_Tube Light Points-(No.) | Tube Light Points | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21522_PASSENGERS LIFTS WORK | 6390_Tube Lights Fixing-(No.) | Tube Lights Fixing | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21523_METER ROOM WORK | 6391_Providing & Fixing 40/32-amp 4 pole 10kA. MCB with Box Make-(No.) | Providing & Fixing 40/32-amp 4 pole 10kA. MCB with Box Make- INDOASIAN ISI. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21523_METER ROOM WORK | 6392_Providing & Fixing 40/32-amp 2 pole MCB 10kA. with Box Make-(No.) | Providing & Fixing 40/32-amp 2 pole MCB 10kA. with Box Make- INDOASIAN ISI. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21523_METER ROOM WORK | 6393_Providing & Fixing 125 Amp 415-volt MCCB SFU with MS enclos-(No.) | Providing & Fixing 125 Amp 415-volt MCCB SFU with MS enclosure, installation of common meter connection in meter room, make- INDOASIAN ISI. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21523_METER ROOM WORK | 6394_Providing & Fixing 100 Amp 415-volt BUS BAR with installati-(No.) | Providing & Fixing 100 Amp 415-volt BUS BAR with installation of cable connection in meter room Termination shall be covered under Electrical requirement of Lift, W/pump, & common wiring. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21523_METER ROOM WORK | 6395_Providing & Laying Single Phase Meter Board Wiring with 6 s-(No.) | Providing & Laying Single Phase Meter Board Wiring with 6 sq. mm x 2 NOS of Single PVC Copper wire including Brass Clip & Nail. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21523_METER ROOM WORK | 6396_Providing & Laying Three Phase Meter Board Wiring with 6 sq-(No.) | Providing & Laying Three Phase Meter Board Wiring with 6 sq. mm x 4 NOS of Single PVC Copper wire including Brass Clip & Nail. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21523_METER ROOM WORK | 6397_Providing & Laying CT. Type 3 Phase Meter Board Wiring with-(No.) | Providing & Laying CT. Type 3 Phase Meter Board Wiring with 16 sq. mm x 4 NOS of Single PVC Copper wire including Brass Clip & Nail. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21524_WATER PUMP | 6398_Water Pump - Providing & Laying 4 core 6 sq.mm Copper Armor-(Rft.) | Water Pump - Providing & Laying 4 core 6 sq.mm Copper Armored Cable make- RR KABEL/POLYCAB from Main switch, Starter to Water Pump Tank. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21524_WATER PUMP | 6399_Borewell - Providing & Laying 4 core 4 sq.mm Copper Armored-(Rft.) | Borewell - Providing & Laying 4 core 4 sq.mm Copper Armored Cable make- RR KABEL/POLYCAB from Main switch, Starter to Borewell Pump. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21524_WATER PUMP | 6400_Water Pump - Providing & Laying 3 core 2.5 sq.mm Copper Arm-(Rft.) | Water Pump - Providing & Laying 3 core 2.5 sq.mm Copper Armored Cable make- RR KABEL ISI/POLYCAB ISI from Starter to Water Pump Tank. For automatic level control. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21524_WATER PUMP | 6401_Providing & Laying 4 core 50 sq.mm Aluminums Armored Cable-(Rft.) | Providing & Laying 4 core 50 sq.mm Aluminums Armored Cable make- RR KABEL ISI /POLYCAB ISI from meter room BUS-BAR to 63 Amp Main Switches, in Starter area. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21524_WATER PUMP | 6402_Providing & Termination of 50 sq.mm brass Gland. ( TO BE IN-(No.) | Providing & Termination of 50 sq.mm brass Gland. ( TO BE INCUDED IN CABLES ) | 1 | 7_No. | 1 | 0 | 0_ | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21524_WATER PUMP | 6403_Providing & Termination of 4/6 sq.mm brass Gland. ( TO BE I-(No.) | Providing & Termination of 4/6 sq.mm brass Gland. ( TO BE INCUDED IN CABLES ) | 1 | 7_No. | 1 | 0 | 0_ | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21524_WATER PUMP | 6404_Providing & Termination of 50 sq.mm Ring Type Lug. ( TO BE-(No.) | Providing & Termination of 50 sq.mm Ring Type Lug. ( TO BE INCUDED IN CABLES ) | 1 | 7_No. | 1 | 0 | 0_ | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21524_WATER PUMP | 6405_Fixing 3 Phase Pump Starter with Interconnections. ( TO BE-(No.) | Fixing 3 Phase Pump Starter with Interconnections. ( TO BE INCUDED IN CABLES ) | 1 | 7_No. | 1 | 0 | 0_ | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21524_WATER PUMP | 6406_Providing & Fixing 63 Amp 415-volt Main Switch with install-(No.) | Providing & Fixing 63 Amp 415-volt Main Switch with installation of Cable connection in 50 sq.mm cable make- Bharat. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21524_WATER PUMP | 6407_Providing & Fixing 40 Amp 4 Pole MCB with 4-way box install-(No.) | Providing & Fixing 40 Amp 4 Pole MCB with 4-way box installation of Cable connection in Pump room, make- INDO-ASIAN. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21525_NORMAL & ALTERNATE FIREFIGHTING | 6408_Supply installation and commissioning of 315 Amp SFU Change-(No.) | Supply installation and commissioning of 315 Amp SFU Change Over Switch Termination shall be covered under Electrical requirement of Fire cable and Alternate cable connection Make- L&T ISI. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21525_NORMAL & ALTERNATE FIREFIGHTING | 6409_Supply installation and commissioning of 315 Amp SFU Main S-(No.) | Supply installation and commissioning of 315 Amp SFU Main Switch with Enclosure & HRC Fuse, Termination shall be covered under Electrical requirement of Fire cable and Alternate cable connection Make- L&T ISI. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21525_NORMAL & ALTERNATE FIREFIGHTING | 6410_Providing & Laying 4 core 150 sq.mm Aluminum Armored Cable-(Rft.) | Providing & Laying 4 core 150 sq.mm Aluminum Armored Cable make- RR-KABEL ISI/POLYCAB ISI, From Meter Room to Change Over Switch, & Fire Panel and Alternate Meter to Change Over Switch. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21525_NORMAL & ALTERNATE FIREFIGHTING | 6411_Providing & Laying 4 core 50 sq.mm Aluminum Armored Cable m-(Rft.) | Providing & Laying 4 core 50 sq.mm Aluminum Armored Cable make- RR-KABEL ISI/POLYCAB ISI, From Meter Room to Change Over Switch, & Fire Panel and Alternate Meter to Change Over Switch. Making Connection Complete. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21525_NORMAL & ALTERNATE FIREFIGHTING | 6412_16 Amp Domestic Power Point of Fire Hooter ( TO BE INCUDED-(No.) | 16 Amp Domestic Power Point of Fire Hooter ( TO BE INCUDED IN CABLES ) | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21525_NORMAL & ALTERNATE FIREFIGHTING | 6413_Providing & Termination of 150 sq.mm Flanch Type Brass Glan-(No.) | Providing & Termination of 150 sq.mm Flanch Type Brass Gland. ( TO BE INCUDED IN CABLES ) | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21525_NORMAL & ALTERNATE FIREFIGHTING | 6414_Providing & Termination of 150 sq.mm Ring Type Lug. ( TO BE-(No.) | Providing & Termination of 150 sq.mm Ring Type Lug. ( TO BE INCUDED IN CABLES ) | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21525_NORMAL & ALTERNATE FIREFIGHTING | 6415_Providing & Termination of 50 sq.mm Flanch Type Brass Gland-(No.) | Providing & Termination of 50 sq.mm Flanch Type Brass Gland( TO BE INCUDED IN CABLES ) | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21525_NORMAL & ALTERNATE FIREFIGHTING | 6460_Providing & Termination of 50 sq.mm Ring Type Lug-(No.) | Providing & Termination of 50 sq.mm Ring Type Lug. ( TO BE INCUDED IN CABLES ) | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21525_NORMAL & ALTERNATE FIREFIGHTING | 6461_Providing & Fixing 100 Amp 415-volt BUS BAR-(No.) | Providing & Fixing 100 Amp 415-volt BUS BAR with installation of cable connection in meter room Termination shall be covered under Electrical requirement of Fire Lift, & Stack Parking. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21525_NORMAL & ALTERNATE FIREFIGHTING | 6462_Providing & Laying 3 core 2.5 sq.mm Copper Armored Cable-(Rft.) | Providing & Laying 3 core 2.5 sq.mm Copper Armored Cable make- RR KABEL ISI/POLYCAB ISI from Change Over Switch to Fire Hooter at convenient Location. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21526_EARTHING AS PER IEE | 6416_Preparing earthing Piet 4’ x 4’ x 5’ Deep Placing 24” x 24”-(No.) | Preparing earthing Piet 4’ x 4’ x 5’ Deep Placing 24” x 24” x 1/4 mm Thick G.I. Hot Deep Earthing Plate, with 25 mm x 3 mm Earthing Strip of G.I. Conductor Out coming and Piet Filled with required Salt, charcoal, Acid, and sand, with arrangement of inserting salty water, when required. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21526_EARTHING AS PER IEE | 6417_Providing & Laying 25 mm x 4 mm Hot Deep Earthing Strip G.I-(Rft.) | Providing & Laying 25 mm x 4 mm Hot Deep Earthing Strip G.I. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21526_EARTHING AS PER IEE | 6418_Earthing BUS-BAR. ( IF REQUIRED )-(No.) | Earthing BUS-BAR. ( IF REQUIRED ) | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21528_CAR LIFT | 6419_Providing & Laying 4 core 16 sq.mm Copper Armored Cable mak-(Rft.) | Providing & Laying 4 core 16 sq.mm Copper Armored Cable make- RR KABEL ISI/ POLYCAB ISI, from meter room to Car Lift Machine Room RCBO Location. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21528_CAR LIFT | 6420_Providing & Laying 8 SWG X 2 NOS. Leads of Copper/GI. Earth-(Rft.) | Providing & Laying 8 SWG X 2 NOS. Leads of Copper/GI. Earth Conductor from Meter Room to Stack Parking Lift Machine RCBO Location. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21528_CAR LIFT | 6421_Providing & Fixing 100 Amp X 4 Pole RCCB 300mA. with 6way D-(No.) | Providing & Fixing 100 Amp X 4 Pole RCCB 300mA. with 6way DB box, for Car Lift machine room, Termination of 3 Phase Cable Connection, make- INDOASIAN ISI. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21528_CAR LIFT | 6422_Providing & Fixing 25 Amp X 2 Pole RCCB with 4-way DB box,-(No.) | Providing & Fixing 25 Amp X 2 Pole RCCB with 4-way DB box, for Lift machine room & Meter room Termination of 1 Phase Cable Connection, make- INDOASIAN ISI. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21528_CAR LIFT | 6423_Providing & Fixing 16 Amps X 2 Pole MCBs. 10kA. with 2-way-(No.) | Providing & Fixing 16 Amps X 2 Pole MCBs. 10kA. with 2-way DB box, for Car Lift machine room, Termination of single-Phase cable connection, make- INDOASIAN | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21528_CAR LIFT | 6424_Providing & Fixing 100 Amps 415 volts ICTP. Main Switch for-(No.) | Providing & Fixing 100 Amps 415 volts ICTP. Main Switch for Meter Room & Car Lift machine Room, Termination of Three Phase Cable Connection, Make- Bharat. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21528_CAR LIFT | 6425_Providing & Fixing Bulkhead Lamp fitting with 40 watts’ bul-(No.) | Providing & Fixing Bulkhead Lamp fitting with 40 watts’ bulb for Lift duct & Lift Machine Room door. . ( DEVELOPER PROVIDES ) | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21528_CAR LIFT | 6463_Providing and Laying 3 core 2.5 sq.mm Copper Armored Cable-(Rft.) | Providing & Laying 3 core 2.5 sq.mm Copper Armored Cable make- RR KABEL ISI/ POLYCAB ISI, from meter room to Car Lift Machine Room RCBO Location. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21527_STACK PARKING LIFT | 6459_Providing and Laying 8 SWG X 2 NOS. Leads of Copper-(Rft.) | Providing & Laying 8 SWG X 2 NOS. Leads of Copper/GI. Earth Conductor from Meter Room to Stack Parking Lift Machine RCBO Location. ( 2 Nos. of Lead included ) | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21527_STACK PARKING LIFT | 6426_Providing & Laying 4 core 4 sq.mm Copper Armored cable make-(Rft.) | Providing & Laying 4 core 4 sq.mm Copper Armored cable make- RR KABEL ISI/ POLYCAB ISI from meter room to Stack Parking Lift Machine RCBO Location. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21527_STACK PARKING LIFT | 6427_Providing & Fixing 40 Amp 4 pole 10kA. MCBs with Box make--(Rft.) | Providing & Fixing 40 Amp 4 pole 10kA. MCBs with Box make- INDOASIAN ISI. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21527_STACK PARKING LIFT | 6428_Providing & Termination of 4 sq.mm Buster Gland. . ( TO BE-(No.) | Providing & Termination of 4 sq.mm Buster Gland. . ( TO BE INCLUDED IN CABLES ) | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21527_STACK PARKING LIFT | 6429_Providing & Laying 10 sq.mm X 4 core Copper Armoured cable-(Rft.) | Providing & Laying 10 sq.mm X 4 core Copper Armoured cable from Meter room inside MCB Panel Box. | 1 | 134_Rft. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_
71 | 21527_STACK PARKING LIFT | 6430_Providing & Fixing VTPN Distribution Board with 40/25 Amp 4-(No.) | Providing & Fixing VTPN Distribution Board with 40/25 Amp 4 Pole RCBO 300mA. 10kA. with box make- INDOASIAN. | 1 | 7_No. | 1 | 0 | 1_C + S GST 18% IP | 0 | 0_ | 2020-04-01 | 1900-01-01 | 0 |  | 0_